** This bid has been approved as a proprietary purchase, and only the brands and models specified will be considered.**

Scope of Work:

Vendor shall provide all labor and materials to install three (3) OPW Integra 100 automatic tank gauge and leak detection systems on three (3) existing underground generator diesel fuel tanks.

Project Location:

Elayn Hunt Correctional Center

6925 Highway 74

St. Gabriel, LA 70776

Specifications:

Contractor Shall:

-Use camera to locate bung openings on three (3) diesel fuel tanks located at Elayn Hunt Correctional Center

-Break up concrete above each bung opening and dispose of debris

-Remove dirt to uncover bung openings on tanks.

-Add a riser to the bung opening and bring up to grade for probe installation on each of the three (3) tanks.

-Install probes and floats in each exposed riser.

-Add a watertight manway cover over each probe riser on the three (3) diesel tanks to meet 2018 DEQ requirements.

-Run wires from each tank to each generator building for new consoles.

-Fill in dirt around the riser openings on each of the three (3) tanks.

-Re-pour concrete around risers to match original thickness and dimensions.

-Install OPW Integra consoles in the three (3) generator rooms.

- Contractor shall be responsible for damage to underground utilities, structures and piping provided that such were identified during the pre-bid conference.

General Terms and Conditions:

-The Department of Corrections shall be responsible for all electrical to power new consoles.

-All work performed must meet 2018 DEQ requirements as it relates to diesel fuel tanks and leak detection.

-Contractor is required to have the appropriate licenses to perform the requested job.

-Work shall be performed Monday - Friday from 7:00 am - 3:30 pm.  Contact facility coordinator, Keith “Randy” Henderson 225-716-3263

-Vendor representatives are subject to passing a background check.

-All visitors are subject to a search of their vehicles, possessions, and persons. This is necessary to preclude the introduction of weapons, ammunition, explosives, cell phones, alcohol, escape devices, drugs and drug paraphernalia, or other forbidden items or contraband into the prison environment. All searches of visitors will be conducted in accordance with the Department Regulation No. C-02-005 and Penitentiary Directive No. 09.004 and .09.004A.

-Vendor representatives must follow all policy and procedures while performing work on facility grounds.